## Summary
Release Date: May 8, 2019
FINAL
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Summer 2019
SUMMARY
In all of the scenarios studied for the final summer SARA, ERCOT identified a potential need to enter Energy Emergency Alert (EEA) status in order to maintain system reliability. The final summer SARA report includes a forecasted peak demand of 74,853 MW, which is 1,300 MW higher than the all-time peak demand record set last summer on July 19.
“ERCOT is prepared to use the tools and procedures that are in place to maintain system reliability during tight conditions,” said ERCOT President and CEO Bill Magness.
While operating reserves are expected to remain tight, total generation resource capacity has increased to 78,929 MW compared to the preliminary summer SARA released in March. This is due primarily to the expected return of a 365 MW gas-fired unit, increased output from certain units that are undergoing equipment upgrades, and an increase in the amount of DC tie imports, which is now based on what is expected during summer emergency conditions.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2019 - Final
Release Date: May 8, 2019
Forecasted Capacity and Demand
|  | Operational Resources (thermal and hydro), MW | 65206.5848 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3514 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | Less Switchable Capacity Unavailable to ERCOT, MW | -788 | Based on survey responses of Switchable Resource owners
|  | Available Mothballed Capacity, MW | 118 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Capacity from Private Use Networks, MW | 3436.9495 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2016-2018)
|  | Non-Coastal Wind, Peak Average Capacity Contribution, MW | 2884.125 | Based on 15% of installed capacity for non-coastal wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Coastal Wind, Peak Average Capacity Contribution, MW | 1635.948 | Based on 58% of installed capacity for coastal wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 1376.992 | Based on 74% of rated capacity for solar resources (summer season) per Nodal Protocols Section 3.2.6.2.2
|  | Storage, Peak Average Capacity Contribution, MW | 0 | Based on 0% of rated capacity; resources assumed to provide regulation reserves rather than sustained capacity available to meet peak loads
|  | RMR Resources to be under Contract, MW | 0
|  | Capacity Pending Retirement, MW | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
|  | Non-Synchronous Ties, Capacity Contribution, MW | 937.5 | Based on import flows during most recent Energy Emergency Alert (EEA) intervals for the summer season (75% of installed capacity)
|  | Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 201 | Based on in-service dates provided by developers of generation resources
|  | Planned Non-Coastal Wind with Signed IA, Peak Average Capacity Contribution, MW | 152.73 | Based on in-service dates provided by developers and 15% summer capacity contribution for non-coastal wind resources
|  | Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution, MW | 225.562 | Based on in-service dates provided by developers and 58% summer capacity contribution for coastal wind resources
|  | Planned Solar Utility-Scale, Peak Average Capacity Contribution, MW | 27.676 | Based on in-service dates provided by developers and a summer capacity contribution of 74% for solar resources
|  | Planned Storage, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and a summer capacity contribution of 0% for storage resources
| [a] Total Resources, MW |  | 78929.0673
| [b] Peak Demand, MW |  | 74853 | Based on average weather conditions at the time of the summer peak for 2003-2017
| [c] Reserve Capacity [a - b], MW |  | 4076.0673
Range of Potential Risks
|  |  | Forecasted Season Peak Load / Typical Generation Outages | Forecasted Season Peak Load / Extreme Generation Outages | Forecasted Season Peak Load / Extreme Low Wind Output | Extreme Season Peak Load / Typical Generation Outages
|  | Seasonal Load Adjustment | 0 | 0 | 0 | 3303 | Based on summer 2014 weather conditions
|  | Typical Maintenance Outages | 381 | 381 | 381 | 381 | Based on the historical average of maintenance outages for weekday peak hours for June through September, for the last three summer seasons (2016 - 2018)
|  | Typical Forced Outages, Thermal | 3845 | 3845 | 3845 | 3845 | Based on the historical average of forced outages for weekday peak hours for June through September, for the last three summer seasons (2016 - 2018)
|  | 90th Percentile Forced Outages, Thermal | 0 | 2665 | 0 | 0 | Based on historical forced outages assuming a 90% confidence interval
|  | Low Wind Output Adjustment | 0 | 0 | 3938 | 0 | Based on the 10th percentile of wind output associated with the 100 highest Net Load hours (Load minus wind output) for the 2015-2018 summer Peak Load seasons; this wind output level is 960 MW.
| [d] Total Uses of Reserve Capacity |  | 4226 | 6891 | 8164 | 7529
| [e] Capacity Available for Operating Reserves, Normal Operating Conditions [c - d], MW |  | -149.9327 | -2814.9327 | -4087.9327 | -3452.9327 | See the Background tab for additional details
Less than 2,300 MW indicates risk of EEA1

## SummerCapacities
Unit Capacities - Summer
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | CDR ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1205
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1195
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1280
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1280
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 604
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 599
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 437
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 800
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 805
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 805
19 | OAK GROVE SES U1 | 19INR0204 | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 862.5
20 | OAK GROVE SES U2 | 19INR0204 | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 847.5
21 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
22 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
23 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 940
24 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
25 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
26 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 664
27 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 663
28 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
29 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
30 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 157
31 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 157
32 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 164
33 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 157
34 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 157
35 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 319
36 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 150
37 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 150
38 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 233
39 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 143.03
40 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 79.49
41 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 143.03
42 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 144.99
43 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 213.46
44 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 149.68
45 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 149.68
46 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 257.85
47 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 75
48 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 75
49 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 70
50 | CALHOUN (PORT COMFORT) 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS | COASTAL | 2017 | 44
51 | CALHOUN (PORT COMFORT) 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS | COASTAL | 2017 | 44
52 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 163
53 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 163
54 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 178
55 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 70
56 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 62
57 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 101
58 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 69
59 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 63
60 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 103
61 | COLORADO BEND II CT7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS | SOUTH | 2017 | 340.7667
62 | COLORADO BEND II CT8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS | SOUTH | 2017 | 340.7667
63 | COLORADO BEND II ST8 | 18INR0077 | CBECII_STG9 | WHARTON | GAS | SOUTH | 2017 | 455.7667
64 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 169
65 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 165
66 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 165
67 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 144
68 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 178
69 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 188
70 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 178
71 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 188
72 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 287
73 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 162
74 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 204
75 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 115
76 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 169
77 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 169
78 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 182
79 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 165
80 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 157
81 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 157
82 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 165
83 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 157
84 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 157
85 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 406
86 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 406
87 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 147
88 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 147
89 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 169
90 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 145
91 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 145
92 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 168
93 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS | COASTAL | 2000 | 145
94 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS | COASTAL | 2000 | 145
95 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS | COASTAL | 2000 | 75
96 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 143
97 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 143
98 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 141
99 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 141
100 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 198
101 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 198
102 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 210
103 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 211
104 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 210
105 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 213
106 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 149
107 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 149
108 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 168
109 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2006 | 155
110 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2006 | 155
111 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2006 | 295
112 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
113 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
114 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 295
115 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
116 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
117 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 153
118 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 145
119 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 145
120 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 153
121 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
122 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
123 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 170
124 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 170
125 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188
126 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 215
127 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 215
128 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 236
129 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 229
130 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 227
131 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 227
132 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 227
133 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 241
134 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 243
135 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 157
136 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 157
137 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 319
138 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 149
139 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 143
140 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 145.3
141 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 143.7
142 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 204.9
143 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 204.9
144 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 196
145 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 195
146 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 326
147 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 195
148 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 195
149 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 312
150 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 191.2
151 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 191.2
152 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 334.7
153 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 76
154 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 76
155 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
156 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 164
157 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 164
158 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 167
159 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 74
160 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 74
161 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
162 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 72
163 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 72
164 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
165 | RIO NOGALES POWER CTG 1 | 19INR0205 | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 166
166 | RIO NOGALES POWER CTG 2 | 19INR0205 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 150
167 | RIO NOGALES POWER CTG 3 | 19INR0205 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 150
168 | RIO NOGALES POWER STG 4 | 19INR0205 | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 286
169 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
170 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 50
171 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
172 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
173 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 150
174 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 145
175 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
176 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 38
177 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 54
178 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 54
179 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 54
180 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 54
181 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 110
182 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 54
183 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 54
184 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 54
185 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 54
186 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 110
187 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 80.32
188 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 80.32
189 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 80.32
190 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 124.94
191 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 160
192 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 125
193 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
194 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
195 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
196 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
197 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 203
198 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 197
199 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 272
200 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 212.5
201 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 212.5
202 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 280
203 | WOLF HOLLOW 2 CT5 | 18INR0076 | WHCCS2_CT4 | HOOD | GAS | NORTH | 2017 | 323.6
204 | WOLF HOLLOW 2 CT6 | 18INR0076 | WHCCS2_CT5 | HOOD | GAS | NORTH | 2017 | 327.4
205 | WOLF HOLLOW 2 STG6 | 18INR0076 | WHCCS2_STG6 | HOOD | GAS | NORTH | 2017 | 464.4
206 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 18
207 | CASTLEMAN CHAMON 1 |  | CHAMON_CTG_0101 | HARRIS | GAS | HOUSTON | 2017 | 44
208 | CASTLEMAN CHAMON 2 |  | CHAMON_CTG_0301 | HARRIS | GAS | HOUSTON | 2017 | 44
209 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 45
210 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 47
211 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 48
212 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 48
213 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 48
214 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 48
215 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 69
216 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 69
217 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 68
218 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 69
219 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 147
220 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 147
221 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS | PANHANDLE | 2016 | 190
222 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 36
223 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 36
224 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 36
225 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 36
226 | FRIENDSWOOD G |  | FEGC_UNIT1 | HARRIS | GAS | HOUSTON | 2018 | 119
227 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 56
228 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 56
229 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 56
230 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50
231 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 56
232 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 56
233 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2
234 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2
235 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2
236 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 90.1
237 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 87.3
238 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46
239 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
240 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44
241 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
242 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 66
243 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 65
244 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 65
245 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 67
246 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 67
247 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 67
248 | DENTON ENERGY CENTER A |  | DEC_AGR_A | DENTON | GAS | NORTH | 2018 | 56.5
249 | DENTON ENERGY CENTER B |  | DEC_AGR_B | DENTON | GAS | NORTH | 2018 | 56.5
250 | DENTON ENERGY CENTER C |  | DEC_AGR_C | DENTON | GAS | NORTH | 2018 | 56.5
251 | DENTON ENERGY CENTER D |  | DEC_AGR_D | DENTON | GAS | NORTH | 2018 | 56.5
252 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
253 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
254 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
255 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
256 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 63
257 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 64
258 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 64
259 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 64
260 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 65
261 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS | HOUSTON | 2018 | 59
262 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS | HOUSTON | 2018 | 61
263 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS | HOUSTON | 2018 | 49
264 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS | HOUSTON | 2018 | 54
265 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS | HOUSTON | 2018 | 54
266 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS | HOUSTON | 2018 | 52
267 | REDGATE A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3
268 | REDGATE B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3
269 | REDGATE C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3
270 | REDGATE D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3
271 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 100
272 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 100
273 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
274 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 11
275 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 11
276 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 80
277 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 80
278 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
279 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
280 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
281 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
282 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
283 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
284 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
285 | SKY GLOBAL POWER ONE A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7
286 | SKY GLOBAL POWER ONE B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7
287 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 56
288 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 56
289 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 56
290 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 56
291 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 56
292 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 56
293 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
294 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 79
295 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
296 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
297 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
298 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
299 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
300 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
301 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
302 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
303 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
304 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 300
305 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
306 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
307 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 107
308 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 315
309 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420
310 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
311 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
312 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
313 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
314 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
315 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
316 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
317 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
318 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
319 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
320 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
321 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
322 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 17.5
323 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 23.5
324 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 39.5
325 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 70
326 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 118
327 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
328 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
329 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
330 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
331 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
332 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
333 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
334 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
335 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
336 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
337 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 217
338 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
339 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
340 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
341 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
342 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 240
343 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 527
344 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
345 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
346 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
347 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
348 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
349 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
350 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
351 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
352 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
353 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
354 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
355 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
356 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
357 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
358 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 64743.11
359
360 | Operational Resources (Hydro)
361 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
362 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
363 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
364 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
365 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
366 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
367 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
368 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
369 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
370 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
371 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
372 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
373 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
374 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
375 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
376 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
377 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
378 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
379 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
380 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
381 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24
382 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24
383 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
384 | CITY OF GONZALES HYDRO |  | DG_GONZ_HYDRO_GONZ_HYDRO | GONZALES | HYDRO | SOUTH | 1986 | 1.5
385 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
386 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
387 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
388 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
389 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
390 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
391 | Operational Capacity Total (Hydro) | [6 empty] | 556.6
392 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 463.4748
393
394 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | 0
395 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 65206.5848
396
397 | Operational Resources (Switchable)
398 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | PANHANDLE | 2016 | 54
399 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | PANHANDLE | 2016 | 54
400 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | PANHANDLE | 2016 | 54
401 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | PANHANDLE | 2016 | 190
402 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | PANHANDLE | 2016 | 190
403 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 153
404 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 155
405 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 315
406 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 153
407 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 155
408 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 315
409 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 160
410 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 160
411 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 160
412 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
413 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 156
414 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 135
415 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 153
416 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 402
417 | Switchable Capacity Total | [6 empty] | 3514
418
419 | Switchable Capacity Unavailable to ERCOT
420 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -54
421 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -54
422 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | 0
423 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -190
424 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -190
425 | TENASKA FRONTIER STATION |  | FTR_FTR_UNAVAIL | GRIMES | GAS | NORTH | 2016 | -300
426 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -788
427
428 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | GAS |  |  | 118
429
430 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 3475.9495
431 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | -39
432
433 | Operational Resources (Wind)
434 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
435 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
436 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
437 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
438 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2012 | 150
439 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8
440 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND | NORTH | 2017 | 44.9
441 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND | NORTH | 2017 | 55.7
442 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
443 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
444 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
445 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
446 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
447 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
448 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
449 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
450 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
451 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
452 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
453 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
454 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
455 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
456 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
457 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
458 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 50.4
459 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND | WEST | 2017 | 126.5
460 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND | WEST | 2017 | 126.5
461 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
462 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
463 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND | PANHANDLE | 2016 | 100.2
464 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND | PANHANDLE | 2016 | 100.2
465 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
466 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND | WEST | 2017 | 98.9
467 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND | WEST | 2017 | 131.1
468 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND | PANHANDLE | 2017 | 163.2
469 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND | NORTH | 2018 | 200
470 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND | WEST | 2017 | 79.8
471 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND | WEST | 2017 | 75.6
472 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
473 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
474 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
475 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
476 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
477 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
478 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
479 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
480 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
481 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
482 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND | WEST | 2016 | 119.9
483 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
484 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9
485 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100
486 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REGAN AND IRION | WIND | WEST | 2018 | 152.5
487 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REGAN AND IRION | WIND | WEST | 2018 | 147.5
488 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND | SOUTH | 2016 | 52
489 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND | SOUTH | 2016 | 98
490 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND | SOUTH | 2016 | 100
491 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND | WEST | 2017 | 131.1
492 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND | WEST | 2017 | 98.9
493 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
494 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
495 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5
496 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115
497 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 95
498 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND | WEST | 2008 | 102
499 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND | WEST | 2001 | 82.5
500 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7
501 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230
502 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND | SOUTH | 2017 | 96
503 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND | SOUTH | 2017 | 74
504 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND | SOUTH | 2017 | 30
505 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
506 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
507 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110
508 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 78
509 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 76.7
510 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 39
511 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 78
512 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
513 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 106.3
514 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 103.8
515 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
516 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
517 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
518 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100
519 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100
520 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2010 | 49.5
521 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2010 | 51
522 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
523 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
524 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200
525 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND | SOUTH | 2016 | 200
526 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND | SOUTH | 2016 | 110
527 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND | PANHANDLE | 2017 | 115.2
528 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND | PANHANDLE | 2017 | 115.2
529 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
530 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
531 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
532 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
533 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
534 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND | WEST | 2018 | 196.6
535 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
536 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
537 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
538 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD COUNTY | WIND | PANHANDLE | 2017 | 151.2
539 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
540 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
541 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
542 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
543 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
544 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
545 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
546 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 91.9
547 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 86
548 | PYRON WIND 1 |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 121.5
549 | PYRON WIND 2 |  | PYR_PYRON2 | SCURRY AND FISHER | WIND | WEST | 2008 | 127.5
550 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3
551 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103
552 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
553 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND | WEST | 2017 | 121.9
554 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND | WEST | 2017 | 27.4
555 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 114
556 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND | WEST | 2008 | 95
557 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150
558 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND | SOUTH | 2018 | 160
559 | SALT FORK 1 WIND 1 |  | SALTFORK_UNIT1 | DONLEY | WIND | PANHANDLE | 2017 | 64
560 | SALT FORK 1 WIND 2 |  | SALTFORK_UNIT2 | DONLEY | WIND | PANHANDLE | 2017 | 110
561 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
562 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76
563 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
564 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1
565 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
566 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 145
567 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
568 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
569 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | PANHANDLE | 2015 | 102
570 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | PANHANDLE | 2015 | 98
571 | SOUTH PLAINS WIND II A |  | SPLAIN2_WIND21 | FLOYD | WIND | PANHANDLE | 2016 | 148.5
572 | SOUTH PLAINS WIND II B |  | SPLAIN2_WIND22 | FLOYD | WIND | PANHANDLE | 2016 | 151.8
573 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
574 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
575 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96
576 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98
577 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
578 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
579 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7
580 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 42.5
581 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 17
582 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 98.8
583 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 34
584 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 117
585 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 85
586 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 112
587 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 125
588 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND | WEST | 2019 | 150
589 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND | WEST | 2019 | 150
590 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
591 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
592 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
593 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
594 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
595 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
596 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND | NORTH | 2017 | 125.6
597 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND | PANHANDLE | 2016 | 114.9
598 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND | PANHANDLE | 2016 | 142.3
599 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
600 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
601 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 92.3
602 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
603 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
604 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND | WEST | 2017 | 125
605 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND | WEST | 2017 | 125
606 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
607 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
608 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
609 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 19227.5
610 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 15
611
612 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
613 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
614 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
615 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
616 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
617 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
618 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
619 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
620 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
621 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
622 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
623 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
624 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
625 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
626 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
627 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
628 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
629 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
630 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
631 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201
632 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
633 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 2820.6
634 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 58
635
636 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 22048.1
637
638 | Operational Resources (Solar)
639 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
640 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
641 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
642 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50
643 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
644 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
645 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
646 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
647 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
648 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
649 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
650 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 106.4
651 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
652 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
653 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
654 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
655 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
656 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182
657 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
658 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5
659 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
660 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
661 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
662 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5
663 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5
664 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5
665 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5
666 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5
667 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5
668 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10
669 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10
670 | FIFTH GENERATION SOLAR 1 |  | DG_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
671 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3
672 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
673 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10
674 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3
675 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10
676 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2
677 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
678 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
679 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6
680 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
681 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10
682 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
683 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
684 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
685 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
686 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
687 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5
688 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5
689 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5
690 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10
691 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10
692 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5
693 | Operational Capacity Total (Solar) | [6 empty] | 1860.8
694 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 74
695
696 | Operational Resources (Storage)
697 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
698 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
699 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
700 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
701 | OCI ALAMO 1 |  | DG_OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
702 | TOS BATTERY STORAGE |  | DG_TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
703 | Operational Capacity Total (Storage) | [6 empty] | 86.5
704 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0
705
706 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0
707
708 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
709
710 | Non-Synchronous Tie Resources
711 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600
712 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220
713 | EAGLE PASS TIE |  | DC_S | MAVERICK | OTHER | SOUTH |  | 30
714 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100
715 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 150
716 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO | OTHER | SOUTH |  | 150
717 | Non-Synchronous Ties Total | [6 empty] | 1250
718 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 75
719
720 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
721 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2021 | 0
722 | HALYARD HENDERSON | 16INR0045 |  | HENDERSON | GAS | NORTH | 2021 | 0
723 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2021 | 0
724 | HUDSON (BRAZORIA ENERGY G) | 16INR0076 |  | BRAZORIA | GAS | COASTAL | 2019 | 90
725 | MIRAGE | 17INR0022 |  | HARRIS | GAS | HOUSTON | 2019 | 11
726 | VICTORIA CITY (CITYVICT) | 18INR0035 |  | REFUGIO | GAS | COASTAL | 2019 | 0
727 | VICTORIA PORT (VICTPORT) | 17INR0045 |  | CALHOUN | GAS | COASTAL | 2019 | 100
728 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 201
729
730 | Planned Wind Resources with Executed SGIA
731 | ARMSTRONG WIND | 18INR0029 |  | ARMSTRONG | WIND | PANHANDLE | 2020 | 0
732 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND | WEST | 2019 | 0
733 | BLUE SUMMIT II | 18INR0070 |  | WILBARGER | WIND | WEST | 2019 | 102
734 | BLUE SUMMIT WIND III | 19INR0182 |  | WILBARGER | WIND | WEST | 2019 | 0
735 | CABEZON WIND (RIO BRAVO I WIND) | 17INR0005 |  | STARR | WIND | SOUTH | 2019 | 237.6
736 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND | WEST | 2019 | 148.4
737 | CANADIAN BREAKS WIND | 13INR0026 |  | OLDHAM | WIND | PANHANDLE | 2019 | 0
738 | CANYON WIND | 18INR0030 |  | SCURRY | WIND | WEST | 2020 | 0
739 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND | WEST | 2020 | 0
740 | DARMSTADT | 18INR0023 |  | SCHLEICHER | WIND | WEST | 2019 | 0
741 | EASTER WIND | 15INR0063 |  | CASTRO | WIND | PANHANDLE | 2020 | 0
742 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND | WEST | 2020 | 0
743 | FOARD CITY WIND | 19INR0019 |  | FOARD | WIND | WEST | 2019 | 0
744 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND | PANHANDLE | 2020 | 0
745 | GOPHER CREEK WIND | 18INR0067 |  | BORDEN | WIND | WEST | 2019 | 0
746 | GRAPE CREEK WIND | 19INR0156 |  | COKE | WIND | WEST | 2020 | 0
747 | GRIFFIN TRAIL WIND | 20INR0052 |  | KNOX | WIND | WEST | 2020 | 0
748 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND | WEST | 2019 | 0
749 | HART WIND | 16INR0033 |  | CASTRO | WIND | PANHANDLE | 2020 | 0
750 | HIDALGO II WIND | 19INR0053 |  | HIDALGO | WIND | SOUTH | 2019 | 0
751 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND | WEST | 2019 | 0
752 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND | WEST | 2020 | 0
753 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND | WEST | 2021 | 0
754 | LAS LOMAS WIND | 16INR0111 |  | STARR | WIND | SOUTH | 2019 | 0
755 | LOCKETT WIND FARM | 16INR0062b |  | WILBARGER | WIND | WEST | 2019 | 0
756 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND | SOUTH | 2019 | 0
757 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND | WEST | 2020 | 0
758 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2020 | 0
759 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND | WEST | 2020 | 0
760 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND | WEST | 2020 | 0
761 | MESTENO WIND | 16INR0081 |  | STARR | WIND | SOUTH | 2020 | 0
762 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND | PANHANDLE | 2020 | 0
763 | OVEJA WIND | 18INR0033 |  | IRION | WIND | WEST | 2019 | 0
764 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2020 | 0
765 | PRAIRIE HILL WIND | 19INR0100 |  | MCLENNAN | WIND | NORTH | 2020 | 0
766 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND | PANHANDLE | 2020 | 0
767 | RANCHERO WIND | 20INR0011 |  | CROCKETT | WIND | WEST | 2019 | 0
768 | RELOJ DEL SOL WIND | 17INR0025 |  | ZAPATA | WIND | SOUTH | 2020 | 0
769 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND | SOUTH | 2020 | 0
770 | S_HILLS WIND (LITTLE MOUNTAIN WIND) | 12INR0055 |  | BAYLOR | WIND | WEST | 2019 | 30.2
771 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND | WEST | 2020 | 0
772 | TG EAST WIND | 19INR0052 |  | KNOX | WIND | WEST | 2020 | 0
773 | TORRECILLAS WIND | 14INR0045 |  | WEBB | WIND | SOUTH | 2019 | 300.5
774 | VERA WIND | 19INR0051 |  | KNOX | WIND | WEST | 2020 | 0
775 | WHITE MESA WIND | 19INR0128 |  | CROCKETT | WIND | WEST | 2020 | 0
776 | WHITEHORSE WIND | 19INR0080 |  | FISHER | WIND | WEST | 2019 | 0
777 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2021 | 0
778 | WILSON RANCH (INFINITY LIVE OAK WIND) | 12INR0060 |  | SCHLEICHER | WIND | WEST | 2019 | 199.5
779 | WKN AMADEUS WIND | 14INR0009 |  | FISHER | WIND | WEST | 2020 | 0
780 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
781 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2019 | 0
782 | KARANKAWA 2 WIND FARM | 19INR0074 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0
783 | KARANKAWA WIND ALT A | 18INR0014 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 0
784 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
785 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.9
786 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
787 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2019 | 226
788 | PEYTON CREEK WIND | 18INR0018 |  | MATAGORDA | WIND-C | COASTAL | 2019 | 0
789 | EAST RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
790 | Planned Capacity Total (Wind) | [6 empty] | 1407.1
791
792 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 1018.2
793 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 15
794
795 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 388.9
796 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 58
797
798 | Planned Solar Resources with Executed SGIA
799 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 0
800 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2021 | 0
801 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) | 16INR0019 |  | COKE | SOLAR | WEST | 2019 | 30
802 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2020 | 0
803 | FOWLER RANCH | 18INR0039 |  | CRANE | SOLAR | WEST | 2020 | 0
804 | GALLOWAY SOLAR | 19INR0121 |  | CONCHO | SOLAR | WEST | 2020 | 0
805 | GARNET SOLAR | 20INR0021 |  | WILLIAMSON | SOLAR | SOUTH | 2020 | 0
806 | GREASEWOOD SOLAR | 19INR0034 |  | PECOS | SOLAR | WEST | 2020 | 0
807 | HOLSTEIN SOLAR | 19INR0009 |  | NOLAN | SOLAR | WEST | 2020 | 0
808 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b |  | PECOS | SOLAR | WEST | 2019 | 7.4
809 | IP TITAN | 20INR0032 |  | CULBERSON | SOLAR | WEST | 2021 | 0
810 | JUNO SOLAR | 21INR0026 |  | BORDEN | SOLAR | WEST | 2021 | 0
811 | LAPETUS SOLAR 2 | 19INR0185 |  | ANDREWS | SOLAR | WEST | 2019 | 0
812 | LILY SOLAR | 19INR0044 |  | KAUFMAN | SOLAR | NORTH | 2020 | 0
813 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 0
814 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2019 | 0
815 | MISAE SOLAR II | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2020 | 0
816 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2020 | 0
817 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2021 | 0
818 | OBERON SOLAR | 19INR0083 |  | ECTOR | SOLAR | WEST | 2019 | 0
819 | OXY SOLAR | 19INR0184 |  | ECTOR | SOLAR | WEST | 2019 | 0
820 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2020 | 0
821 | PHOEBE SOLAR | 19INR0029 |  | WINKLER | SOLAR | WEST | 2019 | 0
822 | PROSPERO SOLAR | 19INR0092 |  | ANDREWS | SOLAR | WEST | 2020 | 0
823 | QUEEN SOLAR | 19INR0102 |  | UPTON | SOLAR | WEST | 2019 | 0
824 | RAMBLER SOLAR | 19INR0114 |  | TOM GREEN | SOLAR | WEST | 2019 | 0
825 | RAYOS DEL SOL | 19INR0045 |  | CAMERON | SOLAR | COASTAL | 2020 | 0
826 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2020 | 0
827 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2020 | 0
828 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2021 | 0
829 | SHAKES SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2020 | 0
830 | SODA LAKE SOLAR 1 | 18INR0040 |  | CRANE | SOLAR | WEST | 2020 | 0
831 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2020 | 0
832 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2020 | 0
833 | TAYGETE SOLAR | 20INR0054 |  | PECOS | SOLAR | WEST | 2020 | 0
834 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2021 | 0
835 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2020 | 0
836 | WEST OF PECOS SOLAR | 14INR0044 |  | REEVES | SOLAR | WEST | 2019 | 0
837 | Planned Capacity Total (Solar) | [6 empty] | 37.4
838 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 74
839
840 | Planned Storage Resources with Executed SGIA
841 | CASTLE GAP BATTERY |  |  | UPTON | OTHER | WEST | 2018 | 9.9
842 | COMMERCE ST ESS |  |  | BEXAR | OTHER | SOUTH | 2019 | 10
843 | JOHNSON CITY BESS |  |  | BLANCO | OTHER | SOUTH | 2019 | 0
844 | JUNO STORAGE | 21INR0032 |  | BORDEN | OTHER | WEST | 2021 | 0
845 | RABBIT HILL ENERGY STORAGE PROJECT |  |  | WILLIAMSON | OTHER | SOUTH | 2019 | 9.9
846 | Planned Capacity Total (Storage) | [6 empty] | 29.8
847 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 0
848
849 | Seasonal Mothballed Resources
850 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 57
851 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
852 | Total Seasonal Mothballed Capacity | [6 empty] | 118
853
854 | Mothballed Resources
855 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 420
856 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
857 | GIBBONS CREEK U1 (AS OF 10/1/2018) |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
858 | Total Mothballed Capacity | [6 empty] | 1310
859
860 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)*
861 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
862 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
863 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
864 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
865 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
866 | Total Retiring Capacity | [6 empty] | 15.8
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon (1) receipt and ERCOT approval of a new Resource Asset Registration Form (RARF), or (2) the unit owner has submitted, and ERCOT has approved, a Generation Interconnection or Change Request (GINR) application, and the project modifies the installed capacity by at least 10 MW as reported in the GINR request. Projects associated with interconnection change requests that meet the 10 MW size threshold are indicated with a code in the “Generation Interconnection Project Code” column. Projects with more than one unit have capacity change amounts prorated equally across the units. These prorated capacity adjustments are temporary until project owners submit RARFs that reflect updated seasonal MW ratings for each unit.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational capacity formula. These resources are assumed to provide regulation reserves rather than sustained capacity available to meet system peak loads.
* ERCOT is now tracking and accounting for retirements of Registered DG facilities. These biomass facilities actually retired between 2014 and 2016.

## Background
Release Date: May 8, 2019
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses an operating reserve threshold of 2,300 MW to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) may be triggered during the time of the forecasted seasonal peak load. This threshold level is intended to be roughly analogous to the 2,300 MW Physical Responsive Capability (PRC) threshold for EEA1. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 MW reserve capacity threshold is a reasonable indicator for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variation in these parameters is based on historic ranges of the parameter values or known changes expected in the near-term. The SARA report is not intended to indicate the likelihood of any of these scenario outcomes.